## DD-41
Straight Wall (Flush Base) Manhole:
(Following the methodology from Design Data 41 published by the ACPA, 1996)
Problem: |  | Determine if the manhole installation shown below in Fig. 7 is stable with respect to buoyancy, and has a minimum factor of safety of 2.0 as required by the project engineer.
In this straight wall manhole example, it is the weight of the structure itself combined with the downward frictional resistance of the soil surrounding the manhole which resists the upward buoyant force. Shear strength as referred to in soils mechanics is the resistance to sliding of one soil mass against another in a uniform system. Certain analyses (such as the present problem) require the determination of shear strength between dissimilar substances - soil and concrete in this case. This shear strength is an apparant rather than true shear resistance and is more accurately referred to as sliding resistance.
1. Find Weight of Structure where:
| gc | = | 150 |  |  |  |  | unit weight of concrete - lb/ft3
| Di | = | 5 |  |  |  |  | inside diameter of structure - ft
| tw | = | 0.5 |  |  |  |  | wall thickness - ft
| Bd | = | Di + (2∙tw) |  | = | 6 |  | outside diameter of structure - ft
| H | = | 23 |  |  |  |  | height of fill - ft
| tb | = | 1 |  |  |  |  | thickness of bottom slab - ft
| ts | = | 0.67 |  |  |  |  | thickness of top slab - ft
| Dc | = | 3 |  |  |  |  | diameter of cover - ft
| Wcover | = | 500 |  |  |  |  | weight of cover - lb
| Wt | = | Wwalls + Wbase + Wtop + Wcover |  |  |  |  | total structure weight - lb
| Wt | =
| Wt | = | 34514.0237 |  |  |  |  | total structure weight - lb
2. Sliding Resistance
Because a high groundwater condition is being analyzed, the effective unit weight if the saturated soil must be determined.
| gs | = | 120 |  |  |  |  | unit weight dry soil - lb/ft3
| SG | = | 2.75 |  |  |  |  | specific gravity of soil - dimensionless
| gsub | = |  |  |  | = | 76.3636 | effective weight of submerged soil - lb/ft3
Normal Pressure In order to quantify sliding resistance, it is necessary to determine the lateral pressure on the walls of the manhole - Fig. 3 below. As shown in Fig. 7 above, the top of the manhole is at the ground surface and, since we are concerned about flotation, the case will be considered where the ground water elevation is at the top of the manhole.
| f | = | 0.3 |  |  |  | friction coefficient - dimensionless. From Table 1, Design Data 41 (low cohesion soil)
| Ka | = | 0.33 |  |  |  | ratio of lateral to vertical earth pressures. From Table 3, Design Data 41 (wet sand)
| P | = |  |  |  |  | total resultant lateral pressure acting on the manhole - lb/ft
| P | = | 6665.4 |  |  |  | lb/ft
| Rsliding | = |  |  |  |  | surface sliding resistance (downward) - lbs
| Rsliding | = | 37691.949 |  |  |  | lb
3. Buoyant Force
| gw | = | 62.4 |  |  |  | unit weight of water lb/ft3
| B | = |  |  |  |  | upward buoyand force - lb
| B | = | 40579.324 |  |  |  | lb
4. Factor of Safety
Generally, if the weight of the structure is the primary force resisting flotation, then a safety factor of 1.0 is adequate. If, however, friction and/or cohesion are the primary forces resisting flotation, then a higher safety factor would be in order to account for the variability of the soil properties.
| FS | =
| FS | = | 1.7794 |  |  |  | The calculated safety factor is < the required factor of 2.0 stated at the beginning of the problem. Therefore, try an extended base with a 12 in. extension (lip) around the entire diameter as in Fig. 5 below.
5. Weight of Extended Base Structure:
| Db | = | 8 |  |  |  | Diameter of base - ft
| tb(ext) | = | 1 |  |  |  | Thickness of extended base - ft
| H1 | = | 22 |  |  |  | Height of fill to extended base
| H2 | = | 1 |  |  |  | Height of fill of extended base
| Wbase | = | [6 empty] | Wbase | = | 7539.8224 |  | Weight of base - lb
| Wsoil | = | [6 empty] | Wsoil | = | 36945.1296 |  | Weight of soil - lb
| Wtop | = | [6 empty] | Wtop | = | 2131.1779 |  | Weight of top - lb
| Wwalls | = | [6 empty] | Wwalls | = | 27641.6957 |  | Weight of walls - lb
| Wtotal | = | Wbase + Wsoil + Wwalls + Wtop + Wcover | [5 empty] | Wtotal | = | 74757.8256 |  | Total Weight - lb
6. Sliding Resistance
| P | = | 6665.4 | lb |  |  | From Step 2
| f | = | 0.5 |  |  |  | friction coefficient - dimensionless. From Table 3, Design Data
| Rsliding | = |  |  |  |  | surface sliding resistance (downward) - lbs
| Rsliding | = | 83759.8867 | lb
3. Buoyant Force
| gw | = | 62.4 |  |  |  |  | unit weight of water lb/ft3
| B | = | [5 empty] | upward buoyand force - lb
| B | = | 41951.5717 |  |  |  | lb
7. Factor of Safety
| FS | =
| FS | = | 3.7786 | > | 2 |  | \ a satisfactory condition